## Coils
Relay4 | Word | 1001 | True | True | False | Open drain
Vacat2 | Word | 1002 | True | True | False | Open drain output Vacat 2
Vacat3 | Word | 1003 | True | True | False | Open drain output Vacat 3

## Discrete inputs
Relay1 | Word | 12001 | True | True | False | Relay controlled and switched by mamos
Relay2 | Word | 12002 | True | True | False | Relay controlled and switched by mamos
Relay3 | Word | 12003 | True | True | False | Open drain switch
Relay4 | Word | 12004 | True | True | False | User programmable switch on outputs socket board
Relay5 | Word | 12005 | True | True | False | For internal use only. No connections provided
Relay6 | Word | 12006 | True | True | False | For internal use only. No connections provided
Relay7 | Word | 12007 | True | True | False | For internal use only. No connections provided
Relay8 | Word | 12008 | True | True | False | For internal use only. No connections provided
In1 | Word | 12009 | True | True | False | Digital input placed on outputs socket board, allows to restart/terminate the mamos' measurement cycle
In2 | Word | 12010 | True | True | False | Digital input placed on outputs socket board, allows to restart/terminate the mamos' measurement cycle
In3 | Word | 12011 | True | True | False | For internal use only. No connections provided
In4 | Word | 12012 | True | True | False | For internal use only. No connections provided
In5 | Word | 12013 | True | True | False | For internal use only. No connections provided
In6 | Word | 12014 | True | True | False | For internal use only. No connections provided
In7 | Word | 12015 | True | True | False | For internal use only. No connections provided
In8 | Word | 12016 | True | True | False | For internal use only. No connections provided
Valvell | Word | 12017 | True | True | False | Valve in optional AUX gas channel
PumpII | Word | 12018 | True | True | False | Pump for ventilation of AUX channel
Fan1 | Word | 12019 | True | True | False | Main ventilating fan for mamos case
Peltierln | Word | 12020 | True | True | False | Cooling element for mamos MD2 gas dryer, available for compact mamos with MD2 gas dryer only
Vacat2 | Word | 12021 | True | True | False | When switched on connects to ground (GND), Allows for relays connection
Vacat3 | Word | 12022 | True | True | False | When switched on connects to ground (GND), Allows for relays connection
Valve4PdifZeroing | Word | 12023 | True | True | False | Two valves coupled together for differential pressure sensor, switch between work mode (0) and calibration mode (1)
BlowBackValve | Word | 12024 | True | True | False | Blowback valve is a device optional to mamos, in stationary gas probe with automatic cleanning option, allows automatic filter cleanning when mamos is in ventilation mode
PdifZeroing | Word | 12025 | True | True | False | 2 coupled valves for differential pressure sensors calibration in ambient pressure
EvenCycle | Word | 12026 | True | True | False | Measurement cycle odd/even status, especially useful for twin-split mamos and for scheduler work mode
EvenCycleNext | Word | 12027 | True | True | False | Status of next measurement cycle value (as in some measurement modes odd and even cycles are not always alternate)
MeasureMplusA | Word | 12028 | True | True | False | Status for AUX channel additional gas channel where fragile sensors are placed
OverDraft | Word | 12029 | True | True | False | Status for latching time of analogue output last measured ventilation, before the gas sample measurement results reach the correct values
IsMMCSlot | Word | 12030 | True | True | False | Status of MMC/SD card port presence in mamos analyser, placed in the bottom half of front panel
isMMCCard | Word | 12031 | True | True | False | Status of MMC/SD card presence in mamos card port
isAD7705 | Word | 12032 | True | True | False | Status of differential pressure sensor presence
isSwitch | Word | 12033 | True | True | False | Status for mamos mode switch presence
Standby | Word | 12034 | True | True | False | Status for forced standby in long time range working modes of mamos analyser
OverPressure | Word | 12035 | True | True | False | Status of overpressure alarm in mamos pressurised version
AuxOverranged | Word | 12036 | True | True | False | Status of over-range alarm for AUX channel of mamos
DryerError | Word | 12037 | True | True | False | Optional available only with MD2 gas dryer in Compact mamos
FlowToLow | Word | 12038 | True | True | False | Status of too low flow in mamos
NoActivePoints | Word | 12039 | True | True | False | Chosen work mode has no active points of triggering the measurement

## Input registers
MBResult0 | Word | 34001 | True | True | False | #1 LCD measurement result, 2 bytes
MBResult1 | Word | 34002 | True | True | False | #2 LCD measurement result, 2 bytes
MBResult2 | Word | 34003 | True | True | False | #3 LCD measurement result, 2 bytes
MBResult3 | Word | 34004 | True | True | False | #4 LCD measurement result, 2 bytes
MBResult4 | Word | 34005 | True | True | False | #5 LCD measurement result, 2 bytes
MBResult5 | Word | 34006 | True | True | False | #6 LCD measurement result, 2 bytes
MBResult6 | Word | 34007 | True | True | False | #7 LCD measurement result, 2 bytes
MBresult7 | Word | 34008 | True | True | False | #8 LCD measurement result, 2 bytes
MBResultCode0 | Word | 34009 | True | True | False | #1 LCD result code type
MBResultCode1 | Word | 34010 | True | True | False | #2 LCD result code type
MBResultCode2 | Word | 34011 | True | True | False | #3 LCD result code type
MBResultCode3 | Word | 34012 | True | True | False | #4 LCD result code type
MBResultCode4 | Word | 34013 | True | True | False | #5 LCD result code type
MBResultCode5 | Word | 34014 | True | True | False | #6 LCD result code type
MBResultCode6 | Word | 34015 | True | True | False | #7 LCD result code type
MBResultCode7 | Word | 34016 | True | True | False | #8 LCD result code type
MBUnitDP0 | Word | 34017 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #1 LCD
MBUnitDP1 | Word | 34018 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #2 LCD
MBUnitDP2 | Word | 34019 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #3 LCD
MBUnitDP3 | Word | 34020 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #4 LCD
MBUnitDP4 | Word | 34021 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #5 LCD
MBUnitDP5 | Word | 34022 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #6 LCD
MBUnitDP6 | Word | 34023 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #7 LCD
MBUnitDP7 | Word | 34024 | True | True | False | Unit Code (MS byte) and precision point (LS byte) for result #8 LCD
MBAnaoutU1 | Word | 34025 | True | True | False | Volatge value forced in analogue output U1, 2 bytes UINT in mV
MBAnaoutU2 | Word | 34026 | True | True | False | Volatge value forced in analogue output U2, 2 bytes UINT in mV
MBAnaoutU3 | Word | 34027 | True | True | False | Volatge value forced in analogue output U3, 2 bytes UINT in mV
MBAnaoutU4 | Word | 34028 | True | True | False | Volatge value forced in analogue output U4, 2 bytes UINT in mV
MBAnaoutI1 | Word | 34029 | True | True | False | Current value forced in analogue output I1, 2 bytes UINT in mA
MBAnaoutI2 | Word | 34030 | True | True | False | Current value forced in analogue output I2, 2 bytes UINT in mA
MBAnaoutI3 | Word | 34031 | True | True | False | Current value forced in analogue output I3, 2 bytes UINT in mA
MBAnaoutI4 | Word | 34032 | True | True | False | Current value forced in analogue output I4, 2 bytes UINT in mA
MBAnaoutCodeU1 | Word | 34033 | True | True | False | Code for result type in analogue output U1
MBAnaoutCodeU2 | Word | 34034 | True | True | False | Code for result type in analogue output U2
MBAnaoutCodeU3 | Word | 34035 | True | True | False | Code for result type in analogue output U3
MBAnaoutCodeU4 | Word | 34036 | True | True | False | Code for result type in analogue output U4
MBAnaoutCodeI1 | Word | 34037 | True | True | False | Code for result type in analogue output I1
MBAnaoutCodeI2 | Word | 34038 | True | True | False | Code for result type in analogue output I2
MBAnaoutCodeI3 | Word | 34039 | True | True | False | Code for result type in analogue output I3
MBAnaoutCodeI4 | Word | 34040 | True | True | False | Code for result type in analogue output I4

## Holding registers
MBOwnAddress | Word | 43001 | True | True | False | Address (MSB) and Anti-address (LSB) in modbus communication
ModbusPWM | Word | 43002 | True | True | False | PWM setting 0..65535